## Slide 1
2021 Code
Chapter 15 Dental Gas and Vacuum Systems
15.1 Applicability. This chapter shall apply to dental health care facilities that qualify to install dental gas and vacuum piping systems.
15.1.1 Category 1 dental piped gas and piped vacuum system requirements shall be applied in facilities where general anesthesia and deep sedation is performed, as defined in 3.3.68.1 and 3.3.68.2.
15.1.2 Category 2 dental piped gas and piped vacuum system requirements shall be applied in facilities where only moderate and minimal sedation is performed, as defined in 3.3.68.3 and 3.3.68.4.
15.1.3 Category 3 dental piped gas and piped vacuum system requirements shall be applied in facilities where minimal or no sedation is performed, as defined in 3.3.68.4.

## Slide 2
15.1.4 A single facility shall be permitted to include dental gas and vacuum systems for more than one category of dental piped gas and vacuum systems.
15.1.5 An existing system that is not in strict compliance with the requirements of this code shall be permitted to continue in use as long as the authority having jurisdiction has determined that such use does not constitute a distinct hazard to life.
15.1.9 Where the term Responsible Facility Authority is used, that entity shall follow the requirements of 5.1.14.1.
15.3.1 General. Facilities that perform deep sedation and general anesthesia associated with dental treatment shall meet the requirements for Category 1 dental gas and vacuum systems.
15.3.2.1.5 Medical Air Supply Systems. Category 1 systems shall comply with 5.1.3.6, except as follows:
(1) Medical air compressors, dryers, aftercoolers, filters, and regulators shall be permitted to be simplex.

## Slide 3
15.3.2.1.6 Oxygen supply systems using concentrators shall be permitted to consist of two sources, one of which shall be a cylinder header with sufficient cylinder connections for an average day's supply.
15.3.2.1.7 Medical–Surgical Vacuum Systems. Category 1 systems shall comply with 5.1.3.7, except as follows:
(1) Medical–surgical vacuum systems shall be permitted to be simplex.
15.3.2.1.8 WAGD Systems. Category 1 systems shall comply with 5.1.3.8, except as follows:
Medical WAGD pumps shall be permitted to be simplex.
15.3.2.7 Warning Systems. Warning systems associated with Category 1 systems shall provide the master, area, and local alarm functions of a Category 1 system as required in 5.1.9, except as follows:
(1) Warning systems shall be permitted to be a single alarm panel

## Slide 4
15.3.2.11 Support Gases. Category 1 systems shall comply with 5.1.13 except as follows:
(1) Nitrogen source equipment shall be permitted to be installed in enclosures for Category 3 medical gases or in a mechanical room.
(2) Nitrogen source equipment shall include the following:
(a) One or more cylinders of nitrogen NF, sufficient for at least one average day’s supply
(b) A manifold, if primary and secondary cylinders are provided
(c) A line pressure regulating valve
(d) A check valve downstream from the pressure regulating valve
(e) A pressure relief valve set at 50 percent above the normal line pressure and located downstream from the check valve
(f) A pressure relief valve discharge piped to outdoors at a point that will not create a probable hazard and that is turned down to prevent the entry of rain or snow

## Slide 5
15.3.3.1.2 Dental vacuum systems shall include dental vacuum and nitrous oxide scavenging.
15.3.3.4* Dental Air.
15.3.3.4.1 General.
15.3.3.4.1.1 Dental air shall be used as a support gas for driving dental tools and shall be permitted to be used to supply air-driven equipment. Dental compressed air shall not be used for respiration.
15.3.3.4.1.2 Dental air outlets shall not be interchangeable with any other gas outlets, including oxygen, nitrous oxide, medical air, instrument air, and nitrogen.
15.3.3.4.2.2 Air compressors shall be scroll dental, reciprocating dental, or the oil-free dental types.

## Slide 6
15.3.3.6.1.2 Active nitrous oxide scavenging shall include the use of a nasal mask on the patient. The nasal mask shall be connected to a scavenging inlet in the dental vacuum system through a flow-limiting adapter.
15.3.3.6.1.3 Nitrous oxide scavenging inlets shall not be interchangeable with any other vacuum inlets, including medical surgical vacuum, dental vacuum, and WAGD.
15.3.3.6.2 Connection to Dental Vacuum. Scavenging connections to the dental vacuum system shall be a direct high-volume evacuation (HVE) connection to a high-volume vacuum port with a capacity of 45 L/min (1.6 cfm).

## Slide 7
15.3.3.7.2 Piping for Dental Air Systems.
15.3.3.7.2.1 General. Pipe, fittings, and joints in piping for dental compressed air systems shall be in accordance with 15.3.3.7.2.2 through 15.3.3.7.2.5.
15.3.3.7.2.2 Pipe. Pipe under 15.3.3.7.2 shall comply with the following:
(1) ASTM B819, Standard Specification for Seamless Copper Tube for Medical Gas Systems, Type L or K.
(2) ASTM B88, Standard Specification for Seamless Copper Water Tube, Type L or K.
(3) ASTM B280, Standard Specification for Seamless Copper Tubing for Air Conditioning and Refrigeration Field Service, ACR tube (O.D. size).
15.3.3.7.2.3 Copper tube shall be hard temper or annealed (soft temper).

## Slide 8
15.3.3.7.2.4 Fittings. Fittings for piping under 15.3.3.7.2 shall be permitted to be any of the following acceptable joining methods:
(1) Brazed or soldered fittings conforming to ASME B16.22, Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings
(2) Brazed fittings conforming to ANSI/ASME B16.50, Wrought Copper and Copper Alloy Braze-Joint Pressure Fittings
(3) Brazed fittings conforming to ASME B16.22 with socket depths equal to or greater than braze-joint pressure fittings in compliance with ANSI/ASME B16.50
(4) Flared fittings conforming to ASME B16.26, Cast Copper Alloy Fittings for Flared Copper Tubes
(5) Compression fittings (3∕4 in. maximum size)

## Slide 9
15.3.3.7.2.5 Joints. Joints for piping under 15.3.3.7.2 shall
comply with the following:
(1) Joints shall be brazed, soldered, threaded, flared, or the compression type.
(2) Where joints are brazed, they shall comply with the requirements of 15.4.6.
(3) Soldered joints shall be made in accordance with ASTM
B828, Standard Practice for Making Capillary Joints by Soldering of Copper and Copper Alloy Tube and Fittings, using a “lead-free” solder filler metal containing not more than 0.2 percent lead by volume that complies with ASTM B32, Standard Specification for Solder Metal.

## Slide 10
15.3.3.7.3 Piping for Dental Vacuum Systems and Scavenging Systems.
(A) Copper Tube. Copper tubing shall comply with the following:
(1) ASTM B819, Standard Specification for Seamless Copper Tube for Medical Gas Systems, Type L or K
(2) ASTM B88, Standard Specification for Seamless Copper Water Tube, Type L or K
(3) ASTM B280, Standard Specification for Seamless Copper Tubing for Air Conditioning and Refrigeration Field Service, ACR tube (O.D. size)
(B) Copper tube shall be hard temper or annealed (soft temper).

## Slide 11
15.3.3.7.3.3 PVC Plastic Piping. PVC plastic piping under
15.3.3.7.3 shall be in accordance with the following:
(1) PVC plastic pipe shall be Schedule 40 or Schedule 80, conforming to ASTM D1785, Standard Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120.
(2) PVC plastic fittings shall be Schedule 40 or Schedule 80 to match the pipe, conforming to ASTM D2466, Standard Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40, or ASTM D2467, Standard Specification Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80.
(3) Joints in PVC plastic piping shall be solvent-cemented in accordance with ASTM D2672, Standard Specification for Joints for IPS PVC Pipe Using Solvent Cement.
15.3.3.7.3.4 CPVC Plastic Piping. CPVC plastic piping under 15.3.3.7.3 shall be in accordance with the following:

## Slide 12
(1) CPVC IPS plastic pipe shall be Schedule 40 or Schedule 80, conforming to ASTM F441/F441M, Standard Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe, Schedules 40 and 80.
(2) CPVC IPS plastic fittings shall be Schedule 40 or Schedule 80 to match the pipe, conforming to ASTM F438, Standard Specification for Socket-Type Chlorinated Poly (Vinyl Chlorinated) (CPVC) Plastic Pipe Fittings, Schedule 40, or ASTM F439, Standard Specification for Chlorinated Poly (Vinyl Chlorinated) (CPVC) Plastic Pipe Fittings, Schedule 80.
(3) CPVC CTS plastic pipe and fittings 1∕2 in. through 2 in. size shall be SDR 11, conforming to ASTM D2846/D2846M, Standard Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Hot- and Cold-Water Distribution Systems.
(4) Solvent cement for joints in CPVC plastic piping shall comply with ASTM F493, Solvent Cements for CPVC Pipe and Fittings.

## Slide 13
15.4 Category 2 Dental Gas and Vacuum Systems.
15.4.1.2 The medical gases shall be limited to oxygen and nitrous oxide.
15.4.1.5 All connections within Category 2 medical gas (oxygen and nitrous oxide) shall be gas-specific to prevent cross-connections with other piping systems, including vacuum, water, and dental air.
15.4.1.6 Station outlets and piped outlets for Category 2 medical gas and dental air having nonstandard operating pressures shall comply with the following additional requirements:
(1) Be gas-specific.
(2) Be pressure-specific where a single gas is piped at more than one operating pressure.
(3) Be a D.I.S.S connection if operated at a gauge pressure in excess of 550 kPa (80 psi).

## Slide 14
(4) Be designed to prevent the removal of the adapter until the pressure has been relieved, if operated at a gauge pressure between 1380 kPa and 2070 kPa (200 psi and 300 psi).
15.4.2.1 Installer Qualifications (Oxygen and Nitrous Oxide).
15.4.2.1.1 Installers of medical gas systems shall be certified in accordance with ASSE 6010, Professional Qualification Standard for Medical Gas Systems Installers, regardless of the capacity of the source equipment.
15.4.2.1.2 Installers of medical gas systems shall not use their certification to oversee installation by noncertified personnel.
15.4.2.1.3 Brazing of medical gas piping systems shall be performed by individuals who are qualified in accordance with 15.4.6.1.

## Slide 15
15.4.2.1.4 Prior to any installation work involving brazing, the installer of the medical gas piping systems shall provide documentation required by 15.4.6.1 for the qualifications of the brazing procedures and individual brazers.
15.4.2.2.3 Liquid containers shall have additional product identification visible from all directions with a minimum of 51 mm (2 in.) high letters such as a 360-degree wraparound tape for medical liquid containers.
N 15.4.2.2.4 Cryogenic liquid containers shall be provided with gas-specific outlet connections in accordance with the mandatory requirements of CGA V-5, Diameter-Index Safety System (Noninterchangeable Low Pressure Connections for Medical Gas Applications), or CGA V-1, Standard for Compressed Gas Cylinder Valve Outlet and Inlet Connections.

## Slide 16
15.4.2.3.12 Cylinders in use and in storage shall be prevented from reaching temperatures in excess of 52°C (125°F).
15.4.2.3.13 Central supply systems for nitrous oxide and carbon dioxide using cylinders or portable containers shall be prevented from reaching temperatures lower than the recommendations of the central supply system's manufacturer but shall never be lower than −7°C (20°F) or greater than 52°C (125°F).
15.4.2.4.1 Gas storage locations in facilities with Category 2 medical gas systems with a total of all gases in cylinders or containers, except nitrogen, connected and in storage at one time that does not exceed 85 m3 (3000 ft3) at standard temperature and pressure (STP), or 142 m3 (5000 ft3) (STP) if oxygen is stored in a DOT specification 4 L (cryogenic liquid) container shall comply with 15.4.2.4.3 through 15.4.2.4.13.

## Slide 17
15.4.2.4.4 Storage of full or empty gas cylinders, or both, shall be permitted in the same enclosure.
15.4.2.4.5 Air compressors, vacuum pumps, and other equipment shall not be located in enclosures for medical gas cylinders (oxygen and nitrous oxide source equipment).
15.4.2.4.11 Outdoor enclosures that are adjacent to a building wall shall be located such that the distance to any window or door of the adjacent building is greater than 3.05 m (10 ft).
15.4.2.5.7 Hose and flexible connectors shall have a gauge pressure rating not less than 6895 kPa (1000 psi).
15.4.2.5.8 Materials used in central supply systems shall meet the following requirements:
(1) In those portions of systems intended to handle oxygen at gauge pressures equal to or greater than 2413 kPa (350 psi), interconnecting hose shall contain no polymeric materials.

## Slide 18
15.4.2.5.9 Nonmetallic hoses and flexible connectors shall not exceed 1.52 m (5 ft) in length and shall not be concealed or penetrate walls, floors, ceilings, or partitions.
15.4.2.6 Emergency Shutoff Valves (Oxygen and Nitrous Oxide).
15.4.2.6.2* Where a central medical gas supply is remote from a single treatment facility, the main supply line shall be provided with an emergency shutoff valve located in the single treatment facility so as to be accessible from all use-point locations in an emergency.

## Slide 19
15.4.2.7.5 Factory-installed copper inlet tubes on station outlets extending no further than 205 mm (8 in.) from the body of the terminal shall be not less than DN8 (NPS 1∕4) (3∕8 in. O.D.) size, with 8 mm (0.3 in.) minimum inside diameter.
15.4.5.3 Minimum Pipe Sizes. The minimum size of the following piping shall be as follows:
(1) Category 2 oxygen piping shall be not less than DN10 (NPS 3∕8 in.) (1∕2 in. O.D.) size.
(2) Category 2 nitrous oxide piping shall be not less than DN8 (NPS 1∕4 in.) (3∕8 in. O.D.) size.
Table 15.4.5.6.5 Maximum Copper Tube Support Spacing
Table 15.4.5.6.6 Maximum Plastic Pipe Support Spacing

## Slide 20
15.4.6.8.4 Joints exhibiting the following conditions shall not be permitted:
(1) Flux or flux residue (where flux or flux-coated BAg rods are used with dissimilar metals)
(2) Base metal melting or erosion
(3) Unmelted filler metal
(4) Failure of the filler metal to be clearly visible all the way around the joint at the interface between the socket and the tube
(5) Cracks in the tube or component
(6) Cracks in the filler metal
(7) Failure of the joint to hold the test pressure under the installer-performed initial pressure test (see 15.4.7.4.4) and standing pressure test (see 15.4.7.4.6)

## Slide 21
15.4.7.1.1.1 Inspection and testing shall be performed on all new piped oxygen and nitrous oxide systems, additions, renovations, temporary installations, or repaired systems to ensure, by a documented procedure, that the following have been completed:
(1) All applicable provisions of this code have been adhered to.
(2) System integrity has been achieved or maintained.
(3) Piping systems are ready for testing and verification.
(4) Piping systems are performing in accordance with their design requirements.
15.4.7.1.1.2 The inspection and testing reports shall be submitted directly to the party that contracted for the testing, who shall submit the reports through channels to the responsible Facility authority and any others that are required.

## Slide 22
15.4.7.3 Qualification of System Testers and Verifiers (Oxygen and Nitrous Oxide).
15.4.7.3.1 Individuals who perform the initial and final tests of the oxygen and nitrous oxide piping systems shall be certified to ASSE 6010, Professional Qualifications Standard for Medical Gas Systems Installers, or verifiers who comply with 15.4.7.3.2.
15.4.7.3.2 Individuals who verify the oxygen and nitrous oxide piping systems shall be certified to ASSE 6030, Professional Qualifications Standard for Medical Gas Systems Verifiers.

## Slide 23
15.4.7.4.3 Initial Cross-Connection Test for Copper Piping Systems.
15.4.7.4.3.5 The system under test shall be charged with oil-free, dry nitrogen NF to a gauge pressure of 345 kPa (50 psi).